**SECURITHERM thermostatic basin mixer**

Single hole, sequential thermostatic mixer H. 95mm L. 120mm

Stopcocks and Hygiene lever L. 100mm, Ø 15mm

Reference: **H960015L**

Specification description

Deck-mounted SECURITHERM thermostatic basin mixer.

Sequential thermostatic mixer: opens and closes with cold water.

No risk of cross flow between hot and cold water.

No non-return valves on the inlets.

Anti-scalding failsafe: shuts off automatically if cold or hot water supply fails.

Securitouch thermal insulation prevents burns.

Single hole mixer with straight spout, H. 95mm L. 120mm, fitted with a hygienic flow straightener, no build-up of impurities and withstands thermal shocks.

Scale-resistant thermostatic sequential cartridge for single control adjustment of flow rate and temperature.

Adjustable temperature from cold water up to 40°C with maximum temperature limiter set at 40°C.

Thermal and chemical shocks are possible.

Spout and body with smooth interiors and low water volume.

Flow rate limited to 5 lpm at 3 bar.

No manual contact thanks to the Hygiene lever L. 100mm.

Without pop-up waste

PEX flexibles F3/8" with chrome-plated brass stopcocks, filters and Ø 15mm conical connectors.

Reinforced fixing via 2 stainless steel rods.

Mixer ideal for healthcare facilities, retirement and care facilities, hospitals and clinics.

Mixer is suitable for people with reduced mobility.

Mixer with 30-year warranty.

Also available with copper tails.