**SECURITHERM thermostatic basin mixer**

Single hole sequential thermostatic mixer, H. 95mm L. 120mm

Hygiene lever L. 100mm, copper tails

Reference: **H9600610L**

Specification description

Deck-mounted thermostatic SECURITHERM basin mixer.

Sequential thermostatic mixer: opens and closes with cold water.

No risk of cross flow between hot and cold water.

No non-return valve on the inlets.

Anti-scalding failsafe: shuts off automatically if cold or hot water supply fails.

Securitouch thermal insulation prevents burns.

Single hole mixer with curved spout H. 95mm L. 120mm fitted with a hygienic flow straightener, no build-up of impurities and withstands thermal shocks.

Scale-resistant sequential thermostatic cartridge for single control of flow rate and temperature.

Temperature can be adjusted from cold water up to 40°C with maximum temperature limiter set at 40°C.

Thermal and chemical shocks are possible.

Body and spout with smooth interiors and low water volume.

Flow rate limited to 5 lpm at 3 bar.

No manual contact thanks to Hygiene control lever L. 146mm.

Without pop-up waste.

Supplied with copper tails and stopcocks in chrome-plated brass.

Reinforced fixing via 2 stainless steel rods.

Mixer ideal for healthcare facilities, retirement and care homes, hospitals and clinics.

Mixer suitable for people with reduced mobility.

30-year warranty.

Also available with PEX flexibles.