**SECURITHERM sequential thermostatic basin mixer**

Single hole sequential thermostatic mixer H. 95mm L. 120mm

Stopcocks and Hygiene lever L. 146mm

Reference: **H9601**

Specification description

Deck-mounted SECURITHERM thermostatic basin mixer.

Thermostatic sequential mixer: opens and closes with cold water.

No risk of cross flow between the hot and cold water.

No non-return valves on the inlets.

Single hole mixer with curved spout H. 95mm L. 120mm fitted with a hygienic flow straightener for no impurity retention and thermal shock-resistant.

Anti-scalding failsafe: shuts off automatically if the cold or hot water supply fails.

Securitouch thermal insulation prevents burns.

Scale-resistant sequential thermostatic cartridge for single lever control of flow rate and temperature.

Temperature can be adjusted from cold water up to 40°C with temperature limiter set at 40°C.

Thermal or chemical shocks are possible.

Body and spout with smooth interiors and low water volume.

Flow rate limited to 5 lpm at 3 bar.

No manual contact thanks to Hygiene control lever L. 146mm.

Ergonomic brass pop-up waste 11/4".

Supplied with PEX flexibles F3/8" with chrome-plated brass stopcocks.

Fixing reinforced via 2 stainless steel rods.

Thermostatic mixer ideal for healthcare facilities, retirement and care homes, hospitals and clinics.

Suitable for people with reduced mobility.

30-year warranty.

Also available with copper tails.